## Slide 1: PowerPoint 8: Safe isolation
PowerPoint presentation
1. Health and safety in building services engineering
1.8 Safe isolation of systems

## Slide 2: Objectives
By the end of the session learners should be able to:
  understand types of system in the BSE sector
  demonstrate how to safely isolate different systems
  complete all required documentation when safely isolating systems.

## Slide 3: Types of system
When working in the BSE sector there are many types of system that you may have to work on, and it is of the utmost importance that you are aware of the main isolation techniques for these.
However, it is of equal importance that the isolation procedure is completed safely and as set out in the various guidance documents.
The three main types of system that you will need to isolate are:
  water supplies (hot and cold)
  gas supplies
  electrical supplies.

## Slide 4: Safe isolation of water supplies
When working on a cold or hot water supply, it is important to know how to safely isolate the system. Remember that if the incoming cold main is isolated at the stop valve, both hot and cold water supplies should be isolated.
The Water Supply (Water Fittings) Regulations 1999 state that there should be an isolation valve at the inlet of all hot and cold terminal fittings to aid localised isolation of the water supply and minimise wastage of water.

## Slide 5: Safe isolation of water supplies
At the point of isolation a notice should be displayed informing people that a plumber is working on the system so that it is not inadvertently turned on while it is being worked on.
Warning
Plumber working on the system – do not turn water on!

## Slide 6: Safe isolation of gas supplies
When working on a gas supply, it is important to know how to safely isolate the system. Only a Gas Safe registered engineer can work on gas systems and appliances. It is however important for us to know how to safely isolate a gas supply in the event of an emergency.
As stated in the Gas Safety (Installation and Use) Regulations 1998, there should be an isolation valve at the inlet of all gas appliances to aid localised isolation of the supply.

## Slide 7: Safe isolation of gas supplies
In the event of an emergency the consumer can isolate a gas supply using the emergency control valve (ECV) next to the gas meter. The ECV should:
      fall to the ‘off’ position
      have on/off tape indicating the direction to close the valve
      move freely.

## Slide 8: Safe isolation of gas supplies
At the point of isolation a notice should be displayed informing people that a gas engineer is working on the system so that it is not inadvertently turned on while it is being worked on.
Warning
Gas engineer working on the system – do not turn
gas on!

## Slide 9: Safe isolation of electrical supplies
For electrical supplies is important to remember that if the main incoming electrical supply is isolated at the mains consumer unit (MCU), then the electrical supply to the entire system will be isolated.
However, each individual circuit will have
its own miniature circuit breaker (MCB),
allowing isolation of individual circuits.
Isolation must be proved using the
safe isolation procedure described next.

## Slide 10: Safe isolation of electrical supplies
When isolating electrical supplies, it is important to follow this procedure to ensure there is no voltage in the supply:
Obtain permission to start work. In some environments a permit to work may be needed.
Identify and, if necessary, trace the circuit to be isolated. This is necessary because you cannot rely on circuit designation alone.
Test with an approved voltage indicating device and proving unit, or a known fixed supply such as the mains.
Use a voltage and continuity tester to verify equipment.
Identify methods of isolation, including storage of any keys.
It is recommended that you fit an appropriate lock-off device and locks in accordance with local requirements.

## Slide 11: Safe isolation of electrical supplies
Attach a warning label for isolation and identified work.
Verify the equipment is isolated by using the approved voltage indicator to verify the circuit is dead (LN-LE-NE). In a 3-phase circuit, this would involve 10 checks in all.
Re-test with an approved voltage indicating device and proving unit, or a known fixed supply such as the mains.
It should now be safe to carry out circuit work, but always check and recheck to verify this.
Remember, it should never be assumed that equipment is dead just because a particular isolation device has been switched to ‘off’. For more detail, visit:
https://www.hse.gov.uk/pubns/priced/gs38.pdf
https://www.electricalsafetyfirst.org.uk/media/1201/best-practice-guide-2-issue-3.pdf

## Slide 12: Safe isolation of electrical supplies
Approved voltage indicating device and proving unit
Electrical circuit isolated using an MCB lock-off kit

## Slide 13: Safe isolation of electrical supplies
At the point of isolation a notice should be displayed informing people that an engineer is working on the electrical system so that it is not inadvertently turned on while it is being worked on.
In some instances the erection of a barrier provides further protection against inadvertent reactivation of the supply.
Warning
Engineer working on the system – do not turn electricity on!

## Slide 14
Any questions?