12. Building services engineering (BSE) systems

# Worksheet 16: Earthing arrangements (tutor)

- In small groups, choose one of the following earthing arrangements:

- TN-S

- TN-C-S

- TT

Prepare a presentation explaining how the electrical supply is earthed in the arrangement.

Include a sketch of the arrangement labelled to show the cables, consumer unit, earthing terminal and how it is earthed.

You can research online to help you to complete the task. You may find useful resources here:

earthing-your-questions-answered.pdf (theiet.org)

An introduction to earthing and bonding (electricalapprentice.co.uk)

Nominate a team member to present back to the class and explain the components of the earthing arrangement and their connections.

TN-S

- The MET is connected to the consumer unit earth bar where all protective conductors are connected.

- The equipotential bonding conductors are also connected to the MET.

- The MET is then connected to the metal sheath of the incoming mains cable providing a fault path to earth.

TN-C-S

- The MET is connected to the consumer unit earth bar where all the final circuits earth conductors are connected.

- The earth equipotential bonding conductors are also connected to the MET.

- The MET is then connected to the neutral link via a protective earthing neutral (PEN) conductor of the incoming mains cable, providing a fault path to earth.

TT

- The MET is connected to an external phosphor bronze electrode driven into the ground with a small connection chamber for the earth conductor. The supply transformers are earthed in the same manner as the system in question.