12. Building services engineering (BSE) systems

# Worksheet 6: Heating systems quiz (tutor)

- Which type of boiler is best suited to a small single dwelling with one kitchen and one bathroom?

A combi boiler.

- Which type of heating system is the most common in industrial and commercial environments?

A two-pipe parallel return system.

- What is the main feature of a two-pipe reverse return system?

It has the flow and return pipes flowing in the same direction.

- Briefly describe the features and function of a low loss header system.

A low loss header is a large diameter pipe which is connected to the boiler(s). Because of its large diameter the primary water flows through it very slowly compared to the distribution pipe – therefore there is a low resistance to flow.

Secondary circuits are then connected to the header with a pump to circulate the secondary water.

Several secondary circuits can be connected for different zones of the heating system.

Compensated circuits can also be installed allowing the building to respond to outside variations in temperature.

- Name two advantages of having several smaller boilers in a large plant room.

Smaller boiler units are cheaper to buy and replace. One could be replaced easily without disruption to the system. The boilers can also be programmed to operate so that all the boilers share the duty, thus prolonging life expectancy.

- List four types of heat emitter and explain where they are used.

Steel panel convector heat emitters (radiators) are used in smaller spaces singly or in multiple.

Fan convector heat emitters are used in large spaces such as schools and workshops.

Unit heaters are designed for large heat outputs and are generally used in factories and other large spaces where noise is not a factor.

Radiant ceiling panel heat emitters are used in hospitals and medical centres. They free up wall space for other equipment.